## Scenario summary
Scenarios | Unnamed: 1 | Unnamed: 2 | Unnamed: 3
Voltage | Generation level | Scenario | Reactive Test
0.95 PU | 0 | PV generation (With BESS Q support) | Leading
0.25
0.5
| 0.75 |  | Lagging
1
1.00 PU | 0 | PV only (With BESS Q support) | Leading
0.25
0.5
| 0.75 |  | Lagging
1
1.05 PU | 0 | PV only (With BESS Q support) | Leading
0.25
0.5
| 0.75 |  | Lagging
1
0.95 PU | 0 | BESS Discharging (With PV Q support) | Leading
0.25
0.5
| 0.75 |  | Lagging
1
1.00 PU | 0 | BESS Discharging (With PV Q support) | Leading
0.25
0.5
| 0.75 |  | Lagging
1
1.05 PU | 0 | BESS Discharging (With PV Q support) | Leading
0.25
0.5
| 0.75 |  | Lagging
1
0.95 PU | 0 | BESS Charging (With PV Q support) | Leading
0.25
0.5
| 0.75 |  | Lagging
1
1.00 PU | 0 | BESS Charging (With PV Q support) | Leading
0.25
0.5
| 0.75 |  | Lagging
1
1.05 PU | 0 | BESS Charging (With PV Q support) | Leading
0.25
0.5
| 0.75 |  | Lagging
1
0.95 PU | 0 | Nighttime | Leading
0.25
0.5
| 0.75 |  | Lagging
1
1.00 PU | 0 | Nighttime | Leading
0.25
0.5
| 0.75 |  | Lagging
1
1.05 PU | 0 | Nighttime | Leading
0.25
0.5
| 0.75 |  | Lagging
1

## Scenario 100%_Power
Scenario | Voltage | Generation level | Configuration | Reactive Test | Target real power (kW) | Simulation results - Real power at POI (kW) | Target reactive power (kVAR) | Simulation results - Reactive power at POI (kVAR) | Gross Active Power Supplied Per PV Skid (kW) | Gross Active Power Supplied Per BESS Skid (kW) | Gross Reactive Power Supplied Per PV Skid (kVAR) | Gross Reactive Power Supplied Per BESS Skid (kVAR) | BESS INV PF | PV INV PF | Simulation results - Power Factor at POI | PASS/FAIL
1 | 0.975 | 1 | PV (with BESS IDLE) | Lagging | 125000 | 125340.384 | 41100 | 42831.274 | 3780 | 0 | 1900 | 0 | - |  | 0.94985 | PASS
2 | 0.975 | 1 | PV (with BESS IDLE) | Leading | 125000 | 125459.985 | -41100 | -43007.245 | 3779.983 | 0 | -650.015 | 0 | - |  | 0.94978 | PASS
3 | 1 | 1 | PV (with BESS IDLE) | Lagging | 125000 | 125352.691 | 41100 | 42600.163 | 3780.008 | 0 | 1879.997 | 0 | - |  | 0.9497 | PASS
4 | 1 | 1 | PV (with BESS IDLE) | Leading | 125000 | 125571.789 | -41100 | -41488.885 | 3780.002 | 0 | -624.991 | 0 | - |  | 0.95009 | PASS
5 | 1.025 | 1 | PV (with BESS IDLE) | Lagging | 125000 | 125500.639 | 41100 | 41485.924 | 3779.983 | 0 | 1819.983 | 0 | - |  | 0.94905 | PASS
6 | 1.025 | 1 | PV (with BESS IDLE) | Leading | 125000 | 125492.002 | -41100 | -42030.107 | 3779.999 | 0 | -649.999 | 0 | - |  | 0.95028 | PASS
7 | 0.975 | 1 | BESS discharging (with PV IDLE) | Lagging | 125000 | 125637.414 | 41100 | 42699.355 | 0 | 1990 | 0 | -890 |  | - | 0.94773 | PASS
8 | 0.975 | 1 | BESS discharging (with PV IDLE) | Leading | 125000 | 125679.498 | -41100 | -42609.05 | 0 | 1990 | 0 | 450 |  | - | 0.94716 | PASS
9 | 1 | 1 | BESS discharging (with PV IDLE) | Lagging | 125000 | 125648.956 | 41100 | 42502.799 | 0 | 1990 | 0 | -880 |  | - | 0.94857 | PASS
10 | 1 | 1 | BESS discharging (with PV IDLE) | Leading | 125000 | 125680.552 | -41100 | -42118.069 | 0 | 1990 | 0 | 450 |  | - | 0.94848 | PASS
11 | 1.025 | 1 | BESS discharging (with PV IDLE) | Lagging | 125000 | 125671.719 | 41100 | 42480.938 | 0 | 1990 | 0 | -870 |  | - | 0.94822 | PASS
12 | 1.025 | 1 | BESS discharging (with PV IDLE) | Leading | 125000 | 125692.025 | -41100 | -41681.654 | 0 | 1990 | 0 | 450 |  | - | 0.94717 | PASS
13 | 0.975 | 1 | BESS Charging (with PV IDLE) | Lagging | -125000 | -125549.823 | 41100 | 42812.685 | 0 | -1935 | 0 | -890 |  | - | 0.9481 | PASS
14 | 0.975 | 1 | BESS Charging (with PV IDLE) | Leading | -125000 | -125513.017 | -41100 | -41076.118 | 0 | -1935 | 0 | 430 |  | - | 0.94926 | PASS
15 | 1 | 1 | BESS Charging (with PV IDLE) | Lagging | -125000 | -125534.101 | 41100 | 43330.596 | 0 | -1935 | 0 | -890 |  | - | 0.94897 | PASS
16 | 1 | 1 | BESS Charging (with PV IDLE) | Leading | -125000 | -125506.995 | -41100 | -42657.725 | 0 | -1935 | 0 | 460 |  | - | 0.94833 | PASS
17 | 1.025 | 1 | BESS Charging (with PV IDLE) | Lagging | -125000 | -125534.993 | 41100 | 43513.425 | 0 | -1935 | 0 | -890 |  | - | 0.94833 | PASS
18 | 1.025 | 1 | BESS Charging (with PV IDLE) | Leading | -125000 | -125497.519 | -41100 | -42906.725 | 0 | -1935 | 0 | 470 |  | - | 0.94774 | PASS
19 | 0.975 | 1 | PV and BESS combined | Lagging | 250000 | 250405.41 | 82200 | 83376.489 | 3500 | 2120 | 2500 | -960 |  |  | 0.94964 | PASS
20 | 0.975 | 1 | PV and BESS combined | Leading | 250000 | 250833.584 | -82200 | -82686.35 | 3499.994 | 2120 | -240.023 | 250 |  |  | 0.94948 | PASS
21 | 1 | 1 | PV and BESS combined | Lagging | 250000 | 250462.176 | 82200 | 84602.043 | 3500.02 | 2120 | 2500.003 | -950 |  |  | 0.94959 | PASS
22 | 1 | 1 | PV and BESS combined | Leading | 250000 | 250881.816 | -82200 | -83610.171 | 3499.988 | 2120 | -260.001 | 280 |  |  | 0.94673 | PASS
23 | 1.025 | 1 | PV and BESS combined | Lagging | 250000 | 250539.588 | 82200 | 83660.726 | 3499.964 | 2120 | 2450.013 | -930 |  |  | 0.9493 | PASS
24 | 1.025 | 1 | PV and BESS combined | Leading | 250000 | 250930.871 | -82200 | -82138.385 | 3500.001 | 2120 | -270 | 280 |  |  | 0.94917 | PASS
25 | 0.975 | 0 | Night time (neutral) | N/A | 0 | -1019.038 | 0 | 0.744 | 0 | 0 | -37 | 10 | - | - | N/A | PASS
26 | 1 | 0 | Night time (neutral) | N/A | 0 | -1019.25 | 0 | 11.502 | 0 | 0 | -33 | 12 | - | - | N/A | PASS
27 | 1.025 | 0 | Night time (neutral) | N/A | 0 | -1021.101 | 0 | 5.864 | 0 | 0 | -36 | 10 | - | - | N/A | PASS
28 | 0.975 | 0 | Native | N/A | 0 | 125341.674 | 0 | -19136.244 | 3769.992 | 0 | -0.001 | 0 | - |  | N/A | PASS
29 | 1 | 0 | Native | N/A | 0 | 125024.049 | 0 | -18582.826 | 3760 | 0 | 0 | 0 | - |  | N/A | PASS
30 | 1.025 | 0 | Native | N/A | 0 | 125033.315 | 0 | -18211.171 | 3760 | 0 | 0.001 | 0 | - |  | N/A | PASS
31 | 0.975 | 0 | Night time (injecting) | N/A | 0 | 1217 | -41100 | 42181 | 0 | 0 | 1250 | 0 | - | - | N/A | PASS
32 | 1 | 0 | Night time (injecting) | N/A | 0 | 1216 | -41100 | 42218 | 0 | 0 | 1250 | 0 | - | - | N/A | PASS
33 | 1.025 | 0 | Night time (injecting) | N/A | 0 | 1216 | -41100 | 42200 | 0 | 0 | 1250 | 0 | - | - | N/A | PASS
34 | 0.975 | 0 | Night time (absorbing) | N/A | 0 | 1100 | 25625 | -26263 | 0 | 0 | -800 | 0 | - | - | N/A | PASS
35 | 1 | 0 | Night time (absorbing) | N/A | 0 | 1218 | 41100 | -41173 | 0 | 0 | -1225 | 0 | - | - | N/A | PASS
36 | 1.025 | 0 | Night time (absorbing) | N/A | 0 | 1217 | 41100 | -41125 | 0 | 0 | -1225 | 0 | - | - | N/A | PASS
37 | 1.025 | 0 | LF 0 | N/A | 0 | 1216 | -41100 | 42200 | 0 | 0 | 1250 | 0 | - | - | N/A | PASS
38 | 0.975 | 0 | LF 25 | N/A | 0 | 1100 | 25625 | -26263 | 0 | 0 | -800 | 0 | - | - | N/A | PASS
39 | 1 | 0 | LF 50 | N/A | 0 | 1218 | 41100 | -41173 | 0 | 0 | -1225 | 0 | - | - | N/A | PASS
40 | 1.025 | 0 | LF 75 | N/A | 0 | 1217 | 41100 | -41125 | 0 | 0 | -1225 | 0 | - | - | N/A | PASS

## Scenario_100_inv_voltages
Scenario | Voltage | Generation level | Configuration | Reactive Test | Highest Inverter LV Voltage (%) | Lowest Inverter LV Voltage (%) | Highest Collector System MV Voltage (%) | Lowest Collector System MV Voltage (%) | MPT1 HS OLTC Tap(%) | PASS/FAIL
1 | 0.975 | 1 | PV (with BESS IDLE) | Leading | 1.061 | 1.01 | 1.021 | 1.01 | 0 | PASS
2 | 0.975 | 1 | PV (with BESS IDLE) | Lagging | 0.993 | 0.987 | 0.998 | 0.993 | 4.3739 | PASS
3 | 1 | 1 | PV (with BESS IDLE) | Leading | 1.059 | 1.008 | 1.019 | 1.008 | -2.5014 | PASS
4 | 1 | 1 | PV (with BESS IDLE) | Lagging | 0.996 | 0.99 | 1.001 | 0.996 | 1.8754 | PASS
5 | 1.025 | 1 | PV (with BESS IDLE) | Leading | 1.067 | 1.018 | 1.029 | 1.018 | -3.7507 | PASS
6 | 1.025 | 1 | PV (with BESS IDLE) | Lagging | 0.996 | 0.99 | 1.001 | 0.996 | -0.62609 | PASS
7 | 0.975 | 1 | BESS discharging (with PV IDLE) | Leading | 1.025 | 1.01 | 1.01 | 1.01 | 0 | PASS
8 | 0.975 | 1 | BESS discharging (with PV IDLE) | Lagging | 0.994 | 0.99 | 0.994 | 0.993 | 4.3739 | PASS
9 | 1 | 1 | BESS discharging (with PV IDLE) | Leading | 1.023 | 1.008 | 1.009 | 1.008 | -2.5014 | PASS
10 | 1 | 1 | BESS discharging (with PV IDLE) | Lagging | 0.996 | 0.992 | 0.996 | 0.995 | 1.8754 | PASS
11 | 1.025 | 1 | BESS discharging (with PV IDLE) | Leading | 1.033 | 1.019 | 1.019 | 1.019 | -3.7507 | PASS
12 | 1.025 | 1 | BESS discharging (with PV IDLE) | Lagging | 0.997 | 0.993 | 0.997 | 0.996 | -0.62609 | PASS
13 | 0.975 | 1 | BESS Charging (with PV IDLE) | Leading | 1.015 | 1.006 | 1.007 | 1.006 | 0 | PASS
14 | 0.975 | 1 | BESS Charging (with PV IDLE) | Lagging | 0.991 | 0.981 | 0.991 | 0.99 | 4.3739 | PASS
15 | 1 | 1 | BESS Charging (with PV IDLE) | Leading | 1.02 | 1.012 | 1.012 | 1.012 | -1.8754 | PASS
16 | 1 | 1 | BESS Charging (with PV IDLE) | Lagging | 0.992 | 0.981 | 0.992 | 0.991 | 1.8754 | PASS
17 | 1.025 | 1 | BESS Charging (with PV IDLE) | Leading | 1.012 | 0.997 | 1.003 | 0.997 | -5 | PASS
18 | 1.025 | 1 | BESS Charging (with PV IDLE) | Lagging | 0.992 | 0.982 | 0.992 | 0.992 | -0.62609 | PASS
19 | 0.975 | 1 | PV and BESS combined | Leading | 1.087 | 1.04 | 1.036 | 1.025 | -2.5014 | PASS
20 | 0.975 | 1 | PV and BESS combined | Lagging | 0.997 | 0.99 | 0.996 | 0.991 | 5.6261 | PASS
21 | 1 | 1 | PV and BESS combined | Leading | 1.09 | 1.043 | 1.04 | 1.028 | -4.3739 | PASS
22 | 1 | 1 | PV and BESS combined | Lagging | 0.998 | 0.991 | 0.998 | 0.992 | 3.1246 | PASS
23 | 1.025 | 1 | PV and BESS combined | Leading | 1.09 | 1.044 | 1.041 | 1.03 | -6.2493 | PASS
24 | 1.025 | 1 | PV and BESS combined | Lagging | 1 | 0.993 | 1 | 0.994 | 0.62609 | PASS
25 | 0.975 | 0 | Night time (neutral) | N/A | 0.999 | 0.998 | 1 | 0.999 | 2.4986 | PASS
26 | 1 | 0 | Night time (neutral) | N/A | 1 | 0.999 | 1 | 1 | 0 | PASS
27 | 1.025 | 0 | Night time (neutral) | N/A | 0.993 | 0.992 | 0.993 | 0.993 | -3.1246 | PASS
28 | 0.975 | 0 | Native | N/A | 1.01 | 0.997 | 1.004 | 0.997 | 3.1246 | PASS
29 | 1 | 0 | Native | N/A | 1.011 | 0.999 | 1.005 | 0.999 | 0.62609 | PASS
30 | 1.025 | 0 | Native | N/A | 1.011 | 0.999 | 1.005 | 0.999 | -1.8754 | PASS
31 | 0.975 | 0 | Night time (injecting) | N/A | [5 empty] | PASS
32 | 1 | 0 | Night time (injecting) | N/A | [5 empty] | PASS
33 | 1.025 | 0 | Night time (injecting) | N/A | [5 empty] | PASS
34 | 0.975 | 0 | Night time (absorbing) | N/A | [5 empty] | PASS
35 | 1 | 0 | Night time (absorbing) | N/A | [5 empty] | PASS
36 | 1.025 | 0 | Night time (absorbing) | N/A | [5 empty] | PASS
37 | 1.025 | 0 | LF 0 | N/A | [5 empty] | PASS
38 | 0.975 | 0 | LF 25 | N/A | [5 empty] | PASS
39 | 1 | 0 | LF 50 | N/A | [5 empty] | PASS
40 | 1.025 | 0 | LF 75 | N/A | [5 empty] | PASS

## Scenario_100_Branch_loading
Scenario | Voltage | Generation level | Configuration | Reactive Test | Current through MPT1 (A) | Current through MPT2 (A) | Max allowed current through MPT (A) | Max ISU PV current (A) | Max ISU BESS current (A) | Max allowed current through ISU PV (A) | Max allowed current through ISU BESS (A) | MPT1 % loading | MPT2 % loading | PASS/FAIL
1 | 0.975 | 1 | PV (with BESS IDLE) | Leading | 1134.4 | 1138.3 | 2510.2 | 3598.4 | 0 | 3938.5 | 7649.9 |  |  | PASS
2 | 0.975 | 1 | PV (with BESS IDLE) | Lagging | 1090.3 | 1090.6 | 2510.2 | 3480.2 | 0 | 3938.5 | 7649.9 |  |  | PASS
3 | 1 | 1 | PV (with BESS IDLE) | Leading | 1133.9 | 1137.8 | 2510.2 | 3597.1 | 0 | 3938.5 | 7649.9 |  |  | PASS
4 | 1 | 1 | PV (with BESS IDLE) | Lagging | 1085.6 | 1087.1 | 2510.2 | 3464.6 | 0 | 3938.5 | 7649.9 |  |  | PASS
5 | 1.025 | 1 | PV (with BESS IDLE) | Leading | 1118.2 | 1123.5 | 2510.2 | 3546.5 | 0 | 3938.5 | 7649.9 |  |  | PASS
6 | 1.025 | 1 | PV (with BESS IDLE) | Lagging | 1087.1 | 1087.4 | 2510.2 | 3469.5 | 0 | 3938.5 | 7649.9 |  |  | PASS
7 | 0.975 | 1 | BESS discharging (with PV IDLE) | Leading | 1136.8 | 1139.9 | 2510.2 | 0 | 2561.5 | 3938.5 | 7649.9 |  |  | PASS
8 | 0.975 | 1 | BESS discharging (with PV IDLE) | Lagging | 1091.1 | 1091.7 | 2510.2 | 0 | 2478.7 | 3938.5 | 7649.9 |  |  | PASS
9 | 1 | 1 | BESS discharging (with PV IDLE) | Leading | 1136.4 | 1139.5 | 2510.2 | 0 | 2560.7 | 3938.5 | 7649.9 |  |  | PASS
10 | 1 | 1 | BESS discharging (with PV IDLE) | Lagging | 1088.5 | 1089.1 | 2510.2 | 0 | 2473.4 | 3938.5 | 7649.9 |  |  | PASS
11 | 1.025 | 1 | BESS discharging (with PV IDLE) | Leading | 1123.4 | 1126.4 | 2510.2 | 0 | 2530.8 | 3938.5 | 7649.9 |  |  | PASS
12 | 1.025 | 1 | BESS discharging (with PV IDLE) | Lagging | 1087.6 | 1088.2 | 2510.2 | 0 | 2471.4 | 3938.5 | 7649.9 |  |  | PASS
13 | 0.975 | 1 | BESS Charging (with PV IDLE) | Leading | 1138.5 | 1138 | 2510.2 | 0 | 2525.4 | 3938.5 | 7649.9 |  |  | PASS
14 | 0.975 | 1 | BESS Charging (with PV IDLE) | Lagging | 1087.9 | 1084.6 | 2510.2 | 0 | 2430.4 | 3938.5 | 7649.9 |  |  | PASS
15 | 1 | 1 | BESS Charging (with PV IDLE) | Leading | 1132.6 | 1132.1 | 2510.2 | 0 | 2512.1 | 3938.5 | 7649.9 |  |  | PASS
16 | 1 | 1 | BESS Charging (with PV IDLE) | Lagging | 1090.8 | 1087.4 | 2510.2 | 0 | 2437.5 | 3938.5 | 7649.9 |  |  | PASS
17 | 1.025 | 1 | BESS Charging (with PV IDLE) | Leading | 1142 | 1148.8 | 2510.2 | 0 | 2548.7 | 3938.5 | 7649.9 |  |  | PASS
18 | 1.025 | 1 | BESS Charging (with PV IDLE) | Lagging | 1091.5 | 1088.2 | 2510.2 | 0 | 2439.3 | 3938.5 | 7649.9 |  |  | PASS
19 | 0.975 | 1 | PV and BESS combined | Leading | 2318.9 | 2324.1 | 2510.2 | 3574 | 2692.8 | 3938.5 | 7649.9 |  |  | PASS
20 | 0.975 | 1 | PV and BESS combined | Lagging | 2145.4 | 2146.8 | 2510.2 | 3164.6 | 2592.9 | 3938.5 | 7649.9 |  |  | PASS
21 | 1 | 1 | PV and BESS combined | Leading | 2309.2 | 2314.4 | 2510.2 | 3563 | 2679.5 | 3938.5 | 7649.9 |  |  | PASS
22 | 1 | 1 | PV and BESS combined | Lagging | 2145.4 | 2146.8 | 2510.2 | 3162.2 | 2594.4 | 3938.5 | 7649.9 |  |  | PASS
23 | 1.025 | 1 | PV and BESS combined | Leading | 2295.9 | 2301.1 | 2510.2 | 3537.8 | 2667.4 | 3938.5 | 7649.9 |  |  | PASS
24 | 1.025 | 1 | PV and BESS combined | Lagging | 2141.7 | 2143.1 | 2510.2 | 3157.3 | 2589.3 | 3938.5 | 7649.9 |  |  | PASS
25 | 0.975 | 0 | Night time (neutral) | N/A | 9.7 | 7.8 | 2510.2 | 33.2 | 12 | 3938.5 | 7649.9 |  |  | PASS
26 | 1 | 0 | Night time (neutral) | N/A | 9.7 | 7.9 | 2510.2 | 29.6 | 14.4 | 3938.5 | 7649.9 |  |  | PASS
27 | 1.025 | 0 | Night time (neutral) | N/A | 9.6 | 7.8 | 2510.2 | 32.5 | 12.1 | 3938.5 | 7649.9 |  |  | PASS
28 | 0.975 | 0 | Native | N/A | 1053.8 | 1056.4 | 2510.2 | 3360.5 | 0 | 3938.5 | 7649.9 |  |  | PASS
29 | 1 | 0 | Native | N/A | 1049.7 | 1052.3 | 2510.2 | 3347.4 | 0 | 3938.5 | 7649.9 |  |  | PASS
30 | 1.025 | 0 | Native | N/A | 1049.8 | 1052.5 | 2510.2 | 3347.7 | 0 | 3938.5 | 7649.9 |  |  | PASS
31 | 0.975 | 0 | Night time (injecting) | N/A |  |  | 2510.2 |  |  | 3938.5 | 7649.9 |  |  | PASS
32 | 1 | 0 | Night time (injecting) | N/A |  |  | 2510.2 |  |  | 3938.5 | 7649.9 |  |  | PASS
33 | 1.025 | 0 | Night time (injecting) | N/A |  |  | 2510.2 |  |  | 3938.5 | 7649.9 |  |  | PASS
34 | 0.975 | 0 | Night time (absorbing) | N/A |  |  | 2510.2 |  |  | 3938.5 | 7649.9 |  |  | PASS
35 | 1 | 0 | Night time (absorbing) | N/A |  |  | 2510.2 |  |  | 3938.5 | 7649.9 |  |  | PASS
36 | 1.025 | 0 | Night time (absorbing) | N/A |  |  | 2510.2 |  |  | 3938.5 | 7649.9 |  |  | PASS
37 | 1.025 | 0 | LF 0 | N/A |  |  | 2510.2 |  |  | 3938.5 | 7649.9 |  |  | PASS
38 | 0.975 | 0 | LF 25 | N/A |  |  | 2510.2 |  |  | 3938.5 | 7649.9 |  |  | PASS
39 | 1 | 0 | LF 50 | N/A |  |  | 2510.2 |  |  | 3938.5 | 7649.9 |  |  | PASS
40 | 1.025 | 0 | LF 75 | N/A |  |  | 2510.2 |  |  | 3938.5 | 7649.9 |  |  | PASS